## parameters
| version | converged | name | f_hz | sn_mva
0 | 2.7.0 | FALSE |  | 50 | 1

## bus
| name | vn_kv | type | zone | in_service | kks
0 | Sys 1 | 220 | b |  | TRUE | NPD001Z1ADW03GW100NYW0001
1 | Sys 2 | 220 | b |  | TRUE | NPD001Z1ADW04GW200NYW0001
2 | Bus 1 220 | 220 | b |  | TRUE | NPD001Z1ADA00GY100NYW0001
3 | Bus 2 220 | 220 | b |  | FALSE | NPD001Z1ADB00GY100NYW0001
4 | Bus 1 110 | 110 | b |  | TRUE | NPD001Z2AEA00GY100NYW0001
5 | Bus 2 110 | 110 | b |  | FALSE | NPD001Z2AEB00LY100NXW0101
6 | Bus Load1 110 | 110 | b |  | TRUE | NPD001Z2AEW03GW200NYW0001
7 | Bus Load2 110 | 110 | b |  | TRUE | NPD001Z2AEW04GW200NYW0001
8 | Bus 1 35 | 35 | b |  | TRUE | NPD001C0AHA00GY100NYW0001
9 | Bus 2 35 | 35 | b |  | FALSE | NPD001C0AHB00GY100NYW0001
10 | Bus Load1 35 | 35 | b |  | TRUE | NPD001C0AHW03GW400NYW0001
11 | Bus Load2 35 | 35 | b |  | TRUE | NPD001C0AHW05GW400NYW0001
12 | Bus Load3 35 | 35 | b |  | TRUE | NPD001C0AHW04GW400NYW0001
13 | Bus Load4 35 | 35 | b |  | TRUE | NPD001C0AHW06GW400NYW0001
14 | Bus 1 0.4 | 0.4 | b |  | TRUE | NPD001J0ANS01GY100NYW0001
15 | Bus 2 0.4 | 0.4 | b |  | TRUE | NPD001J0ANS02GY100NYW0001

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type | kks
0 | Load1 110 | 6 | 25.1 | 0.05 | 0 | 0 |  | 1 | TRUE | wye | NPD001Z2AEW03GW200NYW0001
1 | Load2 110 | 7 | 20.1 | -1.05 | 0 | 0 |  | 1 | TRUE | wye | NPD001Z2AEW04GW200NYW0001
2 | Load1 35 | 10 | 10 | -1.05 | 0 | 0 |  | 1 | TRUE | wye | NPD001C0AHW03GW400NYW0001
3 | Load2 35 | 11 | 10.3 | 0.05 | 0 | 0 |  | 1 | TRUE | wye | NPD001C0AHW05GW400NYW0001
4 | Load3 35 | 12 | 10 | 0.05 | 0 | 0 |  | 1 | TRUE | wye | NPD001C0AHW04GW400NYW0001
5 | Load4 35 | 13 | 10.3 | 0.05 | 0 | 0 |  | 1 | TRUE | wye | NPD001C0AHW06GW400NYW0001
6 | Load1 0.4 | 14 | 0.5 | 0.05 | 0 | 0 |  | 1 | TRUE | wye
7 | Load2 0.4 | 15 | 0.5 | 0.05 | 0 | 0 |  | 1 | TRUE | wye

## switch
| bus | element | et | type | closed | name | z_ohm | kks
0 | 0 | 1 | b | CB | TRUE | Q0 | 0.01
1 | 2 | 0 | l | CB | TRUE | Q1 | 0.01 | NPD001Z1ADF03GS120NYW0001
2 | 3 | 1 | l | CB | TRUE | Q2 | 0.01 | NPD001Z1ADF01GS110NYW0001
3 | 2 | 3 | b | CB | TRUE | Q3 | 0.01 | NPD001Z1ADF02GS130NYW0001
4 | 4 | 5 | b | CB | FALSE | Q4 | 0.01 | NPD001Z2AEF02GS130NYW0001
5 | 4 | 2 | l | CB | FALSE | Q5 | 0.01 | NPD001Z2AEF01GS110NYW0001
6 | 5 | 3 | l | CB | FALSE | Q6 | 0.01 | NPD001Z2AEF03GS120NYW0001
7 | 8 | 0 | t3 | CB | TRUE | Q7 | 0.01 | NPD001C0AHF11GS100NYW0001
8 | 9 | 1 | t3 | CB | TRUE | Q8 | 0.01 | NPD001C0AHF12GS100NYW0001
9 | 8 | 4 | l | CB | TRUE | Q9 | 0.01 | NPD001C0AHF03GS100NYW0001
10 | 8 | 5 | l | CB | TRUE | Q10 | 0.01 | NPD001C0AHF05GS100NYW0001
11 | 9 | 6 | l | CB | TRUE | Q11 | 0.01 | NPD001C0AHF04GS100NYW0001
12 | 9 | 7 | l | CB | TRUE | Q12 | 0.01 | NPD001C0AHF06GS100NYW0001
13 | 14 | 0 | t | CB | TRUE | Q13 | 0.01 | NPD001J0ANS01GS137NYW0001
14 | 15 | 1 | t | CB | TRUE | Q14 | 0.01 | NPD001J0ANS02GS101NYW0001
15 | 8 | 9 | b | CB | FALSE | Q15 | 0.01 | NPD001C0AHF01GS100NYW0001

## ext_grid
| name | bus | vm_pu | va_degree | in_service | s_sc_max_mva | rx_max | kks
0 | Line 204 | 0 | 1.05 | 0 | TRUE | 4573 | 0.1 | NPD001Z1ADW04GW200NYW0001

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service | endtemp_degree | kks
0 | line-204 |  | 0 | 2 | 41.5 | 0.051 | 0.42 | 8.594 | 0 | 0.51 | 1 | 1 |  | TRUE | 20 | NPD001Z1ADW04GW200NYW0001
1 | line-203 |  | 1 | 3 | 5.5 | 0.051 | 0.42 | 8.594 | 0 | 0.51 | 1 | 1 |  | TRUE | 20 | NPD001Z1ADW03GW100NYW0001
2 | VL1 110 |  | 4 | 6 | 5.1 | 0.244 | 0.427 | 8.27 | 0 | 0.4 | 1 | 1 |  | TRUE | 20 | NPD001Z2AEW03GW200NYW0001
3 | VL2 110 |  | 5 | 7 | 5.1 | 0.244 | 0.427 | 8.27 | 0 | 0.4 | 1 | 1 |  | TRUE | 20 | NPD001Z2AEW04GW200NYW0001
4 | KL1 35 |  | 8 | 10 | 3.1 | 0.443 | 0.127 | 150 | 0 | 0.199 | 1 | 1 |  | TRUE | 20 | NPD001C0AHW03GW400NYW0001
5 | KL2 35 |  | 8 | 11 | 9.1 | 0.443 | 0.127 | 150 | 0 | 0.199 | 1 | 1 |  | TRUE | 20 | NPD001C0AHW05GW400NYW0001
6 | KL3 35 |  | 9 | 12 | 2.1 | 0.443 | 0.127 | 150 | 0 | 0.199 | 1 | 1 |  | TRUE | 20 | NPD001C0AHW04GW400NYW0001
7 | KL4 35 |  | 9 | 13 | 5.1 | 0.443 | 0.127 | 150 | 0 | 0.199 | 1 | 1 |  | TRUE | 20 | NPD001C0AHW06GW400NYW0001

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service | pt_percent | oltc | kks | power_station_unit
0 | Trafo1 0.4 |  | 8 | 14 | 0.63 | 35 | 0.4 | 6 | 0.1425 | 0.0135 | 0.3375 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE | NPD001C0AHW09GW400NYW0001
1 | Trafo2 0.4 |  | 9 | 15 | 0.63 | 35 | 0.4 | 6 | 0.1425 | 0.0135 | 0.3375 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE |  | FALSE | NPD001C0AHW10GW400NYW0001

## trafo3w
| name | std_type | hv_bus | mv_bus | lv_bus | sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_at_star_point | in_service | vk0_hv_percent | vk0_mv_percent | vk0_lv_percent | vkr0_hv_percent | vkr0_mv_percent | vkr0_lv_percent | vector_group | kks
0 | Trafo 1 |  | 2 | 4 | 8 | 63 | 63 | 38 | 220 | 110 | 35 | 10.5 | 6.5 | 17 | 0.3 | 0.31 | 0.32 | 0.015 | 0.3 | 0 | 0 | [7 empty] | FALSE | TRUE | [7 empty] | NPD001Z1ADT01GT300NYW0001
1 | Trafo 2 |  | 3 | 5 | 9 | 63 | 63 | 38 | 220 | 110 | 35 | 10.5 | 6.5 | 17 | 0.3 | 0.31 | 0.32 | 0.015 | 0.3 | 0 | 0 | [7 empty] | FALSE | TRUE | [7 empty] | NPD001Z1ADT02GT300NYW0001

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## res_bus_sc
| ikss_ka | skss_mw | ip_ka | rk_ohm | xk_ohm
0 | 12.001 | 4573 | 29.6331 | 1.1584 | 11.5845
1 | 11.9955 | 4570.9023 | 29.5925 | 1.1674 | 11.5889
2 | 4.7851 | 1823.3682 | 11.6293 | 3.2749 | 29.0145
3
4 | 2.5772 | 491.0243 | 6.7812 | 1.3852 | 27.0712
5
6
7
8 | 3.7465 | 227.1167 | 10.143 | 0.18071 | 5.9303
9
10 | 3.4133 | 206.9207 | 7.1871 | 1.554 | 6.324
11 | 2.6965 | 163.4652 | 4.5178 | 4.212 | 7.086
12
13
14 | 15.734 | 10.9008 | 42.9828 | 0.00038866 | 0.016141
15

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | bus | kks | object
6 | load | name | object
7 | load | bus | uint32
8 | load | p_mw | float64
9 | load | q_mvar | float64
10 | load | const_z_percent | float64
11 | load | const_i_percent | float64
12 | load | sn_mva | float64
13 | load | scaling | float64
14 | load | in_service | bool
15 | load | type | object
16 | load | kks | object
17 | switch | bus | int64
18 | switch | element | int64
19 | switch | et | object
20 | switch | type | object
21 | switch | closed | bool
22 | switch | name | object
23 | switch | z_ohm | float64
24 | switch | kks | object
25 | ext_grid | name | object
26 | ext_grid | bus | uint32
27 | ext_grid | vm_pu | float64
28 | ext_grid | va_degree | float64
29 | ext_grid | in_service | bool
30 | ext_grid | s_sc_max_mva | int64
31 | ext_grid | rx_max | float64
32 | ext_grid | kks | object
33 | line | name | object
34 | line | std_type | object
35 | line | from_bus | uint32
36 | line | to_bus | uint32
37 | line | length_km | float64
38 | line | r_ohm_per_km | float64
39 | line | x_ohm_per_km | float64
40 | line | c_nf_per_km | float64
41 | line | g_us_per_km | float64
42 | line | max_i_ka | float64
43 | line | df | float64
44 | line | parallel | uint32
45 | line | type | object
46 | line | in_service | bool
47 | line | endtemp_degree | int64
48 | line | kks | object
49 | trafo | name | object
50 | trafo | std_type | object
51 | trafo | hv_bus | uint32
52 | trafo | lv_bus | uint32
53 | trafo | sn_mva | float64
54 | trafo | vn_hv_kv | float64
55 | trafo | vn_lv_kv | float64
56 | trafo | vk_percent | float64
57 | trafo | vkr_percent | float64
58 | trafo | pfe_kw | float64
59 | trafo | i0_percent | float64
60 | trafo | shift_degree | float64
61 | trafo | tap_side | object
62 | trafo | tap_neutral | float64
63 | trafo | tap_min | float64
64 | trafo | tap_max | float64
65 | trafo | tap_step_percent | float64
66 | trafo | tap_step_degree | float64
67 | trafo | tap_pos | float64
68 | trafo | tap_phase_shifter | bool
69 | trafo | parallel | uint32
70 | trafo | df | float64
71 | trafo | in_service | bool
72 | trafo | pt_percent | float64
73 | trafo | oltc | object
74 | trafo | kks | object
75 | trafo | power_station_unit | float64
76 | trafo3w | name | object
77 | trafo3w | std_type | object
78 | trafo3w | hv_bus | uint32
79 | trafo3w | mv_bus | uint32
80 | trafo3w | lv_bus | uint32
81 | trafo3w | sn_hv_mva | float64
82 | trafo3w | sn_mv_mva | float64
83 | trafo3w | sn_lv_mva | float64
84 | trafo3w | vn_hv_kv | float64
85 | trafo3w | vn_mv_kv | float64
86 | trafo3w | vn_lv_kv | float64
87 | trafo3w | vk_hv_percent | float64
88 | trafo3w | vk_mv_percent | float64
89 | trafo3w | vk_lv_percent | float64
90 | trafo3w | vkr_hv_percent | float64
91 | trafo3w | vkr_mv_percent | float64
92 | trafo3w | vkr_lv_percent | float64
93 | trafo3w | pfe_kw | float64
94 | trafo3w | i0_percent | float64
95 | trafo3w | shift_mv_degree | float64
96 | trafo3w | shift_lv_degree | float64
97 | trafo3w | tap_side | object
98 | trafo3w | tap_neutral | float64
99 | trafo3w | tap_min | float64
100 | trafo3w | tap_max | float64
101 | trafo3w | tap_step_percent | float64
102 | trafo3w | tap_step_degree | float64
103 | trafo3w | tap_pos | float64
104 | trafo3w | tap_at_star_point | bool
105 | trafo3w | in_service | bool
106 | trafo3w | vk0_hv_percent | float64
107 | trafo3w | vk0_mv_percent | float64
108 | trafo3w | vk0_lv_percent | float64
109 | trafo3w | vkr0_hv_percent | float64
110 | trafo3w | vkr0_mv_percent | float64
111 | trafo3w | vkr0_lv_percent | float64
112 | trafo3w | vector_group | float64
113 | trafo3w | kks | object
114 | res_bus_sc | ikss_ka | float64
115 | res_bus_sc | skss_mw | float64
116 | res_bus_sc | ip_ka | float64
117 | res_bus_sc | rk_ohm | float64
118 | res_bus_sc | xk_ohm | float64